## Main Sheet
Pointset Abbreviation Naming Schema
The following are the BL point naming schema used for determining the point names: The following example is for a fan_coil_unit_zone_set_point from the naming schema the name = "FCUZnTempStpt":
The device name FCU = is found from the following link
https://github.com/theodi/BDNS/blob/master/BDNS_Abbreviations_Register.csv
Zone = Zn, found in following table.
Temperature = Temp, found in following table.
Setpoint = Stpt, found in following table.
Please note that these are required Cloud Data Points , which is a Subset of the Operational Data Points, and are sent to the cloud using JSON over MQTT Telemetry
The Smart Building Consultant is responsible for ensuring that these data points are exposed at either the direct IoT controller or the Gateway device.

## Points Naming Schema
AC - AC | Discharge - Dschrg | Lift - Lift | Scene | - Scn
Adjust - Adj | Door - Dr | Limit - Lmt | Sensor | - Snsr
Air - Air | Dual - Du | Line - Ln | Serial | - Ser
Alarm - Alrm | Duct - Duct | Link - Lnk | Service | - Srv
Angle - Angl | Due - Due | Load - Ld | Setpoint | - Stpt
Apparent - App | Economizer - Econ | Local - Lcl | Shutdown | - Shtdwn
Around - Arnd | Enable - Enab | Lockout - Lck | Sink | - Snk
Audible - Aud | Energy - Enrgy | Low - Lo | Sleep | - Slp
Auto - Auto | Enrolled - Enrl | Mains - Mains | Smoke | - Smk
Available - Avail | Entering - Ent | Maintenance - Maint | Solar | - Slr
Average - Avg | Enthalpy - Enth | Manufacturer - Man | Space | - Spc
Azimuth - Az | Escalator - Esc | Maximum - Max | Speed | - Spd
Bag - Bag | Events per - Evntper | Measurement - Meas | Stack | - Stk
Band - Bnd | Exhaust - Exh | Message - Msg | Stage | - Stg
Battery - Bat | Extract - Ext | Meter - Mtr | Standby | - Stndby
Beacon - Beac | Factor - Fctr | Minimum - Min | State | - State
Boiler - B | Factored - Fctrd | Mixed - Mix | Station | - Stn
Building - Bldg | Fading - Fd | Mode - Md | Steam | - Stm
Button - Btn | Failure - Fail | Mode - Mode | Step | - Step
Bypass - Byp | Fan - Fan | Model - Mod | Stop | - Stop
Cautionary - Caut | Fault - Flt | Motion - Mtn | Storage | - Strg
Change - Chng | Feedback - Fdbk | Motor - Mot | Supply | - Sup
Charge - Chrg | Filter - Fltr | Name - Name | Switch | - Swtch
Chilled - Chld | Fire - Fire | Number - Num | System | - Sys
Chilled water - CW | Firmware - Firm | Occupied - Occ | Tape | - Tpe
Circuit - Cir | Floor - Flr | On - On | Temperature | - Temp
Circulation - Circ | Flow - Flw | Open - Opn | Thermal | - Thrml
Closed - Cls | Frequency - Freq | Out - Out | Thermostat | - Thrmstat
Coil - Coil | Fresh - Frsh | Overload - Ovld | Time | - Tim
Cold - Cold | Frost - Frst | Overridden - Over | Total | - Tot
Colour - Col | Full - Full | Panel - Pan | Trace | - Trc
Command - Cmd | Fume - Fum | Panel - Pnl | Transformer | - Tr
Common - Com | Gain - Gn | Percent - Pct | Travel | - Trvl
Compressor - Cmp | Gallery - Gal | Period - Per | Type | - Type
Condensate - Cond | Grains - Gr | Phase - Ph | Underfloor | - Undr
Confirmed - Conf | Group number - Grp | Piezoelectric - Piez | Unit | - Unit
Content - Cont | Harmonic - Hrm | Planned - Plnd | Unoccupied | - Unocc
Control - Cntrl | Heat - Heat | Position - Pos | Up | - Up
Cooling - Clg | Heating - Htg | Power - Pwr | Update | - Upd
Cooling - Cool | High - Hi | Pre - Pre | User | - Usr
Count - Cnt | Hold - Hld | Pressure - Pr | Valve | - Vlv
Critical - Crit | Hot - Hot | Proportional - Prp | Variable | - Var
Cumulative - Cum | Hot water - HW | Pump - Pmp | Velocity | - Vel
Current - Crnt | Hours - Hrs | Push - Push | Version | - Ver
Curtailment - Crtlmnt | Humidity - Hum | Rain - Rain | Vibration | - Vbr
Curve - Curv | Illuminance - Ill | Reactive - Reac | Voltage | - Vlt
Cut - Cut | In - In | Read - Rd | Volume | - Vlm
Damper - Dmpr | Incoming - Incom | Reference - Ref | Walk | - Wlk
DC - DC | Increase - Incr | Registers - Reg | Warm | - Wrm
Decrease - Dcr | Input - Inpt | Remote - Rem | Warning | - Warn
Delay - Dly | Instantaneous - Inst | Request - Rqst | Water | - Wtr
Demand - Dmnd | Intake - Intk | Requested - Rqstd | Wheel | - Whl
Details - Det | Integral - Int | Reset - Res | Zenith | - Zen
Detected - Detect | Isolation - Iso | Response - Rsp | Zone | - Zn
Dewpoint - Dwpt | Lag - Lag | Return - Rtrn
Differential - Dif | Lamp - Lmp | Reverse - Rev
Dimming - Dim | Last - Lst | Running - Run
Direction - Dir | Lead - Lead | Sash - Sash
Dirty - Drty | Leak - Lk | Save - Sv
Disable - Dsbl | Level - Lvl

## State Sample(Generic)
Property | Sensor Signal Type | Shadow Data Types | Read/Write (Variable) | Point Abbreviation | Point Type | Payload Interval | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | CoV,24hr | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | CoV,24hr | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | CoV,24hr | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | CoV,24hr | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | CoV,24hr | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | CoV,24hr | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | CoV,24hr | State
Fault Status | N/A | String | R | Flt | SoftPoint | CoV,24hr | State
Serial Number | N/A | String | R | SerNum | SoftPoint | CoV,24hr | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | CoV,24hr | State
Manufacturer | N/A | String | R | Man | SoftPoint | CoV,24hr | State
Temperature Setpoint | N/A | Num,0 | R/W | TempStPt | SoftPoint | CoV,24hr | State/Config
Cooling Setpoint | N/A | Num,0 | R/W | FCUOccCoolStPt | SoftPoint | CoV,24hr | State/Config
Unoccupied Cooling Setpoint | N/A | Num,0 | R | FCUUnoccCoolStPt | SoftPoint | CoV,24hr | State
Unoccupied Heating Setpoint | N/A | Num,0 | R | FCUUnoccHtgStPt | SoftPoint | CoV,24hr | State
Pressure Setpoint | N/A | Num,0 | R | PressStPt | SoftPoint | CoV,24hr | State
Flow Setpoint | N/A | Num,0 | R | FlowStPt | SoftPoint | CoV,24hr | State
Charge Level | N/A | Num,0 | R | BatChrgLev | SoftPoint | CoV,24hr | State
Time to Discharge | N/A | Num,0 | R | BatTmDschrg | SoftPoint | CoV,24hr | State
Time to Charge | N/A | Num,0 | R | BatTmChrg | SoftPoint | CoV,24hr | State
Occupied Mode | DO | Boolean | R | FCUOccMd | Hardwired | 2,2,30s, 30s | Pointset
Chilled Water Valve | AI/AO | Number | R/W | FCUCWVlv | Hardwired | 2,2,30s, 30s | Pointset/Config
Hot Water Valve | AI/AO | Number | R/W | FCUHWVlv | Hardwired | 2,2,30s, 30s | Pointset/Config
Supply Air Temperature | AI | Number | R | FCUSATemp | Hardwired | 2,2,300s, 300s | Pointset
Return Air Temperature | AI | Number | R | FCURATemp | Hardwired | 2,2,300s, 300s | Pointset
Fan Command | DI/DO | Boolean | R/W | FCUFanCmnd | Hardwired | None | Pointset/Config
Fan Speed | AI/AO | Number | R/W | FCUFanSpd | Hardwired | 2,2,300s, 300s | Pointset/Config
Zone Temperature | AI | Number | R | FCUZnTemp | Hardwired | 2,2,300s, 300s | Pointset
Zone Temperature Setpoint | N/A | Number | R | FCUZnTempStPt | SoftPoint | COV,24hr | State
Occupied Cooling Setpoint | N/A | Number | R | FCUOccCoolStPt | SoftPoint | COV,24hr | State
Occupied Heating Setpoint | N/A | Number | R | FCUOccHtgStPt | SoftPoint | COV,24hr | State
Unoccupied Cooling Setpoint | N/A | Number | R | FCUUnoccCoolStPt | SoftPoint | COV,24hr | State
Unoccupied Heating Setpoint | N/A | Number | R | FCUUnoccHtgStPt | SoftPoint | COV,24hr | State

## Pointset example(FCU)
Property | Sensor Signal Type | Shadow Data Type | Read/Write (Variable) | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
Occupied Mode | DO | Boolean | R | FCUOccMd | Hardwired | 2,2,30s, 30s | Pointset
Chilled Water Valve | AI/AO | Number | R/W | FCUCWVlv | Hardwired | 2,2,30s, 30s | Pointset/Config
Hot Water Valve | AI/AO | Number | R/W | FCUHWVlv | Hardwired | 2,2,30s, 30s | Pointset/Config
Supply Air Temperature | AI | Number | R | FCUSATemp | Hardwired | 2,2,300s, 300s | Pointset
Return Air Temperature | AI | Number | R | FCURATemp | Hardwired | 2,2,300s, 300s | Pointset
Fan Command | DI/DO | Boolean | R/W | FCUFanCmnd | Hardwired | None | Pointset/Config
Fan Speed | AI/AO | Number | R/W | FCUFanSpd | Hardwired | 2,2,300s, 300s | Pointset/Config
Zone Temperature | AI | Number | R | FCUZnTemp | Hardwired | 2,2,300s, 300s | Pointset
Zone Temperature Setpoint | N/A | Number | R | FCUZnTempStPt | SoftPoint | COV,24hr | State
Occupied Cooling Setpoint | N/A | Number | R | FCUOccCoolStPt | SoftPoint | COV,24hr | State
Occupied Heating Setpoint | N/A | Number | R | FCUOccHtgStPt | SoftPoint | COV,24hr | State
Unoccupied Cooling Setpoint | N/A | Number | R | FCUUnoccCoolStPt | SoftPoint | COV,24hr | State
Unoccupied Heating Setpoint | N/A | Number | R | FCUUnoccHtgStPt | SoftPoint | COV,24hr | State

## PAC Ctrl
Property | Sensor Signal Type | Shadow Data Type | Read/Write (Variable) | InstGuid | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Number of enrolled users | N/A | Number | Number | NumEnrlUsr | SoftPoint | 2,2,30s, COV | Pointset
List of enrolled user IDs | N/A | JSON Object | Number | EnrlUsrID | SoftPoint | 2,2,30s, COV | Pointset

## PACS Readers
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Instance-type | wiegand connector | String | R | Instance-type | Hardwired | 2,2,30s, 30s | Pointset
Last Read Status | wiegand connector | Boolean | R | LstRdStat | Hardwired | 2,2,30s, 30s | Pointset
Last User ID | wiegand connector | String | R | LstUsrID | Hardwired | 2,2,30s, 30s | Pointset
Last Read Time | wiegand connector | String (RFC 3339) | R | LstRdTm | Hardwired | 2,2,30s, 30s | Pointset

## Turnstiles
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | History | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Instance-type | N/A | String | R | Type | SoftPoint | 2,2,24hr, COV | State
Status | N/A | Boolean | R | Stat | SoftPoint | 2,2,24hr, COV | State
Last Open Time | N/A | String (RFC 3339) | R | LstOpTm | SoftPoint | 2,2,24hr, COV | State

## LightSensor
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Measurement | N/A | Period Number | R/W | LtgSnsrMeas | SoftPoint | 2,2,24hr, COV | State/Config
Update Interval | N/A | Number | R/W | LtgSnsrUpdInt | SoftPoint | 2,2,24hr, COV | State/Config
Illuminance | N/A | Number | R | LtgSnsrIll | SoftPoint | 2,2,24hr, COV | State/Config
Units | N/A | String | R | LtgSnsrUnit | SoftPoint | 2,2,24hr, COV | State

## MotionSensor
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Measurement Period | N/A | Number | R/W | MtnSnsrMeasPer | SoftPoint | 2,2,24hr, COV | State
Update Interval | N/A | Number | R/W | MtnSnsrUpdInt | SoftPoint | 2,2,24hr, COV | State
Motion | N/A | Boolean | R | MtnSnsrMtn | SoftPoint | 2,2,24hr, COV | State

## LTG UI
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
Status | String |  | R | UsrIntStat
Number of States | Number |  | R | UsrIntNumState

## LUMINAIRES
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
On/Off State | N/A | Boolean | R/W | LumOnOffState | SoftPoint | 2,2,24hr, COV | State
Level | N/A | Number | R/W | LumLev | SoftPoint | 2,2,24hr, COV | State /Config
Level Minimum | N/A | Number | R/W | LumLevMin | SoftPoint | 2,2,24hr, COV | State /Config
Level Maximum | N/A | Number | R/W | LumLevMax | SoftPoint | 2,2,24hr, COV | State /Config
Group Number | N/A | Number | R/W | LumGrpNum | SoftPoint | 2,2,24hr, COV | State
Scene Number | N/A | Number | R/W | LumScnNum | SoftPoint | 2,2,24hr, COV | State
Dimming Curve | N/A | String | R/W | LumDimCurv | SoftPoint | 2,2,24hr, COV | State
Transition/Fading Time | N/A | Number | R/W | LumTrnFdTime | SoftPoint | 2,2,24hr, COV | State
Transition/Fading Number of Steps | N/A | Number | R/W | LumTrnFdNumStep | SoftPoint | 2,2,24hr, COV | State
State On Power Up | N/A | String (On/Off/PreviousLevel/Specified Level) | R/W | LumStatePwrUp | SoftPoint | 2,2,24hr, COV | State
Power | N/A | Number | R | LumPwr | SoftPoint | 2,2,24hr, COV | State
Voltage | N/A | Number | R | LumVlt | SoftPoint | 2,2,24hr, COV | State
Hours Run | N/A | Number | R | LumHrsRn | SoftPoint | 2,2,24hr, COV | State

## CAMERAS
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Camera active | N/A | Boolean | R | CamState | SoftPoint | 2,2,24hr, COV | State
Tamper/fault | N/A | Boolean | R | CamFlt | SoftPoint | 2,2,24hr, COV | State
PTZ state | N/A | JSON Object | R | CamAim | SoftPoint | 2,2,24hr, COV | State
Person counter | N/A | Number | R | CamOcc | SoftPoint | 2,2,24hr, COV | State

## ELECT MTR 3PH
Property | Sensor Signal Type |  | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Current Transformer Ratio | AI | Number | R/W | 3PhMtrCurrTrRt | Hardwired | 2,2,30s, 30s | Pointset
Voltage Transformer Ratio | AI | Number | R/W | 3PhMtrVltTrRt | Hardwired | 2,2,30s, 30s | Pointset
L1-N Voltage | AI | Number | R | 3PhMtrL1Vlt | Hardwired | 2,2,30s, 30s | Pointset
L2-N Voltage | AI | Number | R | 3PhMtrL2Vlt | Hardwired | 2,2,30s, 30s | Pointset
L3-N Voltage | AI | Number | R | 3PhMtrL3Vlt | Hardwired | 2,2,30s, 30s | Pointset
Average Phase Voltage | AI | Number | R | 3PhMtrAvgPhVlt | Hardwired | 2,2,30s, 30s | Pointset
L1-L2 Voltage | AI | Number | R | 3PhMtrL1L2Vlt | Hardwired | 2,2,30s, 30s | Pointset
L2-L3 Voltage | AI | Number | R | 3PhMtrL2L3Vlt | Hardwired | 2,2,30s, 30s | Pointset
L3-L1 Voltage | AI | Number | R | 3PhMtrL1L3Vlt | Hardwired | 2,2,30s, 30s | Pointset
Average Line Voltage | AI | Number | R | 3PhMtrAvgLnVlt | Hardwired | 2,2,30s, 30s | Pointset
L1 Current | AI | Number | R | 3PhMtrL1Curr | Hardwired | 2,2,30s, 30s | Pointset
L2 Current | AI | Number | R | 3PhMtrL2Curr | Hardwired | 2,2,30s, 30s | Pointset
L3 Current | AI | Number | R | 3PhMtrL3Curr | Hardwired | 2,2,30s, 30s | Pointset
Average Line Current | N/A | Number | R | 3PhMtrAvgLnCurr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Power | N/A | Number | R | 3PhMtrL1Pwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Power | N/A | Number | R | 3PhMtrL2Pwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Power | N/A | Number | R | 3PhMtrL3Pwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Power | N/A | Number | R | 3PhMtrTotPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Apparent Power | N/A | Number | R | 3PhMtrL1AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Apparent Power | N/A | Number | R | 3PhMtrL2AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Apparent Power | N/A | Number | R | 3PhMtrL3AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Apparent Power | N/A | Number | R | 3PhMtrTotAppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Reactive Power | N/A | Number | R | 3PhMtrL1ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Reactive Power | N/A | Number | R | 3PhMtrL2ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Reactive Power | N/A | Number | R | 3PhMtrL3ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Reactive Power | N/A | Number | R | 3PhMtrTotReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Power Factor | N/A | Number | R | 3PhMtrL1PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Power Factor | N/A | Number | R | 3PhMtrL2PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Power Factor | N/A | Number | R | 3PhMtrL3PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
Average Power Factor | N/A | Number | R | 3PhMtrAvgPwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Energy | N/A | Number | R | 3PhMtrCumEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Reactive Energy | N/A | Number | R | 3PhMtrCumReacEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
AC Frequency | N/A | Number | R | 3PhMtrACFreq | SoftPoint | 2,2,30s, 30s | Pointset
Reset cumulative measurement registers | N/A | Boolean | R/W | 3PhMtrResCumMeasReg | SoftPoint | 2,2,30s, 30s | Pointset

## ELEC MTR 3PH HARMONICS
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Current Transformer Ratio | AI | Number | R/W | 3PhMtrCurrTrRt | Hardwired | 2,2,30s, 30s | Pointset
Voltage Transformer Ratio | AI | Number | R/W | 3PhMtrVltTrRt | Hardwired | 2,2,30s, 30s | Pointset
L1-N Voltage | AI | Number | R | 3PhMtrL1Vlt | Hardwired | 2,2,30s, 30s | Pointset
L2-N Voltage | AI | Number | R | 3PhMtrL2Vlt | Hardwired | 2,2,30s, 30s | Pointset
L3-N Voltage | AI | Number | R | 3PhMtrL3Vlt | Hardwired | 2,2,30s, 30s | Pointset
Average Phase Voltage | AI | Number | R | 3PhMtrAvgPhVlt | Hardwired | 2,2,30s, 30s | Pointset
L1-L2 Voltage | AI | Number | R | 3PhMtrL1L2Vlt | Hardwired | 2,2,30s, 30s | Pointset
L2-L3 Voltage | AI | Number | R | 3PhMtrL2L3Vlt | Hardwired | 2,2,30s, 30s | Pointset
L3-L1 Voltage | AI | Number | R | 3PhMtrL1L3Vlt | Hardwired | 2,2,30s, 30s | Pointset
Average Line Voltage | AI | Number | R | 3PhMtrAvgLnVlt | Hardwired | 2,2,30s, 30s | Pointset
L1 Current | AI | Number | R | 3PhMtrL1Curr | Hardwired | 2,2,30s, 30s | Pointset
L2 Current | AI | Number | R | 3PhMtrL2Curr | Hardwired | 2,2,30s, 30s | Pointset
L3 Current | AI | Number | R | 3PhMtrL3Curr | Hardwired | 2,2,30s, 30s | Pointset
Average Line Current | N/A | Number | R | 3PhMtrAvgLnCurr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Power | N/A | Number | R | 3PhMtrL1Pwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Power | N/A | Number | R | 3PhMtrL2Pwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Power | N/A | Number | R | 3PhMtrL3Pwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Power | N/A | Number | R | 3PhMtrTotPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Apparent Power | N/A | Number | R | 3PhMtrL1AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Apparent Power | N/A | Number | R | 3PhMtrL2AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Apparent Power | N/A | Number | R | 3PhMtrL3AppPwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Apparent Power | N/A | Number | R | 3PhMtrTotAppPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Reactive Power | N/A | Number | R | 3PhMtrL1ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Reactive Power | N/A | Number | R | 3PhMtrL2ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Reactive Power | N/A | Number | R | 3PhMtrL3ReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
Total Reactive Power | N/A | Number | R | 3PhMtrTotReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
L1 Power Factor | N/A | Number | R | 3PhMtrL1PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
L2 Power Factor | N/A | Number | R | 3PhMtrL2PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
L3 Power Factor | N/A | Number | R | 3PhMtrL3PwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
Average Power Factor | N/A | Number | R | 3PhMtrAvgPwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Energy | N/A | Number | R | 3PhMtrCumEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Reactive Energy | N/A | Number | R | 3PhMtrCumReacEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
AC Frequency | N/A | Number | R | 3PhMtrACFreq | SoftPoint | 2,2,30s, 30s | Pointset
Reset cumulative measurement registers | N/A | Boolean | R/W | 3PhMtrResCumMeasReg | SoftPoint | 2,2,30s, 30s | Pointset
L1-N harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL1HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L2-N harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL2HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L3-N harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL3HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L1-N THD(v) | AI | Number | R | 3PhMtrL1THDv | Hardwired | 2,2,30s, 30s | Pointset
L2-N THD(v) | AI | Number | R | 3PhMtrL2THDv | Hardwired | 2,2,30s, 30s | Pointset
L3-N THD(v) | AI | Number | R | 3PhMtrL3THDv | Hardwired | 2,2,30s, 30s | Pointset
L1-L2 harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL1L2HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L2-L3 harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL2L3HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L1-L3 harmonic voltages | AI | Number (h1 to h50) | R | 3PhMtrL1L3HrmVlt | Hardwired | 2,2,30s, 30s | Pointset
L1-L2 THD(v) | AI | Number | R | 3PhMtrL1L2THDv | Hardwired | 2,2,30s, 30s | Pointset
L2-L3 THD(v) | AI | Number | R | 3PhMtrL2L3THDv | Hardwired | 2,2,30s, 30s | Pointset
L1-L3 THD(v) | AI | Number | R | 3PhMtrL1L3THDv | Hardwired | 2,2,30s, 30s | Pointset
L1 harmonic currents | AI | Number (h1 to h50) | R | 3PhMtrL1Curr | Hardwired | 2,2,30s, 30s | Pointset
L2 harmonic currents | AI | Number (h1 to h50) | R | 3PhMtrL2Curr | Hardwired | 2,2,30s, 30s | Pointset
L3 harmonic currents | AI | Number (h1 to h50) | R | 3PhMtrL3Curr | Hardwired | 2,2,30s, 30s | Pointset
L1 THD(i) | AI | Number | R | 3PhMtrL1THDi | Hardwired | 2,2,30s, 30s | Pointset
L2 THD(i) | AI | Number | R | 3PhMtrL2THDi | Hardwired | 2,2,30s, 30s | Pointset
L3 THD(i) | AI | Number | R | 3PhMtrL3THDi | Hardwired | 2,2,30s, 30s | Pointset

## ELEC MTR 1PH
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Current Transformer Ratio | N/A | Number | R/W | 1PhMtrCurrTrRt | SoftPoint | 2,2,30s, 30s | Pointset
Voltage Transformer Ratio | N/A | Number | R/W | 1PhMtrVltTrRt | SoftPoint | 2,2,30s, 30s | Pointset
Voltage | N/A | Number | R | 1PhMtrVlt | hardwired | 2,2,30s, 30s | Pointset
Current | N/A | Number | R | 1PhMtrCurr | hardwired | 2,2,30s, 30s | Pointset
Power | N/A | Number | R | 1PhMtrPwr | SoftPoint | 2,2,30s, 30s | Pointset
Apparent Power | N/A | Number | R | 1PhMtrAppPwr | SoftPoint | 2,2,30s, 30s | Pointset
Reactive Power | N/A | Number | R | 1PhMtrReacPwr | SoftPoint | 2,2,30s, 30s | Pointset
Power Factor | N/A | Number | R | 1PhMtrPwrFctr | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Energy | N/A | Number | R | 1PhMtrCumEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
Cumulative Reactive Energy | N/A | Number | R | 1PhMtrCumReacEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
AC Frequency | N/A | Number | R | 1PhMtrACFreq | SoftPoint | 2,2,30s, 30s | Pointset

## Heat Meters
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Flow Temperature | AI | Number | R | HMtrFlowTemp | Hardwired | 2,2,30s, 30s | Pointset
Return Temperature | AI | Number | R | HMtrRtrnTemp | Hardwired | 2,2,30s, 30s | Pointset
Flow Rate | AI | Number | R | HMtrFlowRate | Hardwired | 2,2,30s, 30s | Pointset
Energy | N/A | Number | R | HMtrEnrgy | SoftPoint | 2,2,30s, 30s | Pointset

## Blinds and Louvres
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Blind Position | N/A | Number (0 to 100 where 100 is fully open, 0 is fully closed) | R/W | BlndP | SoftPoint | 2,2,24hr, COV | State
Blind Motor Running | N/A | Boolean | R | BlndMotRn | SoftPoint | 2,2,24hr, COV | State
Blind Motor Run Time | N/A | Number (seconds) | R | BlndMotRnTm | SoftPoint | 2,2,24hr, COV | State
Blind Motor Overcurrent Alarm | N/A | Boolean | R | BlndMotOvrcurAl | SoftPoint | 2,2,24hr, COV | State
Blind State | N/A | Number | R | BlndState | SoftPoint | 2,2,24hr, COV | State
Status | N/A | String | R | Stat | SoftPoint | 2,2,24hr, COV | State
Number Of States | N/A | Number | R | NumState | SoftPoint | 2,2,24hr, COV | State
Open | N/A | Boolean | R/W | Op | SoftPoint | 2,2,30s, 30s | Pointset/Config
Close | N/A | Boolean | R/W | Cls | SoftPoint | 2,2,30s, 30s | Pointset/Config

## PV Invertors
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Inverter enabled | N/A | Boolean | R | PvInvState | SoftPoint | 2,2,24hr, COV | State
Current export power | N/A | Number | R | PvInvPwr | SoftPoint | 2,2,24hr, COV | State
Inverter temperature | N/A | Number | R | PvInvTemp | Hardwired | 2,2,24hr, COV | State
Alarm or fault | N/A | Boolean | R | PvInvFlt | SoftPoint | 2,2,24hr, COV | State
Blind Position | N/A | Number (0 to 100 where 100 is fully open, 0 is fully closed) | R/W | BlndP | Hardwired | 2,2,30s, 30s | Pointset/Config
Blind Motor Running | N/A | Boolean | R | BlndMotRn | Hardwired | 2,2,30s, 30s | Pointset
Blind Motor Run Time | N/A | Number (seconds) | R | BlndMotRnTm | Hardwired | 2,2,30s, 30s | Pointset
Blind Motor Overcurrent Alarm | N/A | Boolean | R | BlndMotOvrcurAl | Hardwired | 2,2,30s, 30s | Pointset
Blind State | N/A | Number | R/W | BlndState | Hardwired | 2,2,30s, 30s | Pointset/Config
Status | N/A | String | R/W | Stat | Hardwired | 2,2,30s, 30s | Pointset/Config
Number Of States | N/A | Number | R | NumState | Hardwired | 2,2,30s, 30s | Pointset
Open | N/A | Boolean | R/W | Op | Hardwired | 2,2,30s, 30s | Pointset/Config
Close | N/A | Boolean | R/W | Cls | Hardwired | 2,2,30s, 30s | Pointset/Config

## Battery Storage system
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Import/export request | N/A | Abbreviation* | R/W | BatModeReq | SoftPoint | 2,2,24hr, COV | State
Import/export power | N/A | Number | R | BatPwr | SoftPoint | 2,2,24hr, COV | State
Battery energy level | N/A | Number | R | BatChgState | SoftPoint | 2,2,24hr, COV | State
Battery temperature | N/A | Number | R | BatTemp | SoftPoint | 2,2,24hr, COV | State
Battery voltage | N/A | Number | R | BatVlg | SoftPoint | 2,2,24hr, COV | State
Alarm or fault | N/A | Boolean | R | BatFlt | SoftPoint | 2,2,24hr, COV | State

## Sensors
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Measurement Period | N/A | Number | R/W | MeasPer | SoftPoint | 2,2,30s, 30s | Pointset/Config
Update Interval | N/A | Number | R/W | UpdInt | SoftPoint | 2,2,30s, 30s | Pointset/Config
Measured Variable | N/A | Number | R | MeasVar | SoftPoint | 2,2,24hr, COV | State
Unit | N/A | String | R | Unit | SoftPoint | 2,2,24hr, COV | State

## GAS meters
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Pulsed Output | N/A | Number | R | GasMtrPO | hardwired | 2,2,30s, 30s | Pointset

## Fire Detection System
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Pulsed Output | N/A | Number | R | GasMtrPO | hardwired | 2,2,30s, 30s | Pointset

## Beacons LBS
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Location | Wireless | String | R | Loc | SoftPoint | 2,2,30s, 30s | Pointset

## Alarms
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Alarm Status | N/A | String | R | AlStat | SoftPoint | 2,2,30s, 30s | Alarm
Low level Status | N/A | Boolean | R | L/L | SoftPoint | 2,2,30s, 30s | Alarm
Low Low-Level Status | N/A | Boolean | R | LL/L | SoftPoint | 2,2,30s, 30s | Alarm
High Level Status | N/A | Boolean | R | H/L | SoftPoint | 2,2,30s, 30s | Alarm
High High Level Status | N/A | Boolean | R | HH/L | SoftPoint | 2,2,30s, 30s | Alarm
Content Level | N/A | Number | R | ContLev | SoftPoint | 2,2,30s, 30s | Alarm
Content Level Unit | N/A | Number | R | ContLevUnit | SoftPoint | 2,2,30s, 30s | Alarm
Cut-Off Alarm Status | N/A | Boolean | R | CtOffAlStat | SoftPoint | 2,2,30s, 30s | Alarm

## VSD
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Speed | N/A | Number | R/W | InvSpd | SoftPoint | 2,2,30s, 30s | Pointset
VSD Alarm | N/A | Boolean | R | InvAl | SoftPoint | 2,2,30s, 30s | Pointset
VSD "Out of Auto"/Remote Mode and in Local Mode | N/A | Boolean | R | InvOutAutRemMdLocMd | SoftPoint | 2,2,30s, 30s | Pointset
Motor Power | N/A | Number | R | InvMotPwr | SoftPoint | 2,2,30s, 30s | Pointset
Motor kWh | N/A | Number | R | InvMotEnrgy | SoftPoint | 2,2,30s, 30s | Pointset
Motor Current | AI | Number | R | InvMotCurr | Hardwired | 2,2,30s, 30s | Pointset
Motor Voltage | AI | Number | R | InvMotVlt | Hardwired | 2,2,30s, 30s | Pointset
Run Hours | N/A | Number | R | InvHrsRn | SoftPoint | 2,2,30s, 30s | Pointset
Motor Vibration | AI | Number | R | InvMotVbr | Hardwired | 2,2,30s, 30s | Pointset
DC Link Voltage | AI | Number | R | InvDCLnkVlt | Hardwired | 2,2,30s, 30s | Pointset
Motor Temperature | AI | Number | R | InvMotTemp | Hardwired | 2,2,30s, 30s | Pointset
Thermal Overload on VSD | AI | Boolean | R | InvThrmlOvld | Hardwired | 2,2,30s, 30s | Pointset
Heat sink temperature | AI | Number | R | InvHeatSnkTemp | Hardwired | 2,2,30s, 30s | Pointset

## Actuators
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Position Command | AI | Number | R/W | ActrPosCmnd | Hardwired | 2,2,30s, 30s | Pointset/Config
Position | AI | Number | R | ActrPos | Hardwired | 2,2,30s, 30s | Pointset
Open position | DI | Boolean | R | ActrOpPos | Hardwired | 2,2,30s, 30s | Pointset
Closed position | DI | Boolean | R | ActrClPos | Hardwired | 2,2,30s, 30s | Pointset

## AHU
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
AHU Hot Water Valve Position Command | AI | Number | R/W | AHUHWVv1ActrPosCmnd | Hardwired | 2,2,30s, 30s | Pointset/Config
AHU Hot Water Valve Position | AI | Number | R | AHUHWVv1ActrPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Hot Water Valve Open position | DI | Boolean | R | AHUHWVv1ActrOpPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Hot Water Valve Closed position | DI | Boolean | R | AHUHWVv1ActrClPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Cold Water Valve Position Command | AI | Number | R/W | AHUHWVv1ActrPosCmnd | Hardwired | 2,2,30s, 30s | Pointset/Config
AHU Cold Water Valve Position | AI | Number | R | AHUHWVv1ActrPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Cold Water Valve Open position | DI | Boolean | R | AHUHWVv1ActrOpPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Cold Water Valve Closed position | DI | Boolean | R | AHUHWVv1ActrClPos | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Fan Command | AO | Boolean | R/W | AHUSupFanCmd | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Fan Running Status | DI | Boolean | R | AHUSupFanRnStat | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Fan Speed Feedback | DI | Abbreviation* | R | AHUSupFanSpdFdbk | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Fan VFD Speed Status | AI | Number | R | AHUSupFanVFDSpdStat | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Fan VFD Frequency | AI | Number | R | AHUSupFanVFDFrq | Hardwired | 2,2,30s, 30s | Pointset
AHU Extract Fan Command | AO | Boolean | R/W | AHUExtFanCmd | Hardwired | 2,2,30s, 30s | Pointset
AHU Extract Fan Running Status | DI | Boolean | R | AHUExtFanRnStat | Hardwired | 2,2,30s, 30s | Pointset
AHU Extract Fan Speed Feedback | DI | Abbreviation* | R | AHUExtFanSpdFdbk | Hardwired | 2,2,30s, 30s | Pointset
AHU Extract Fan VFD Speed Status | AI | Number | R | AHUExtFanVFDSpdStat | Hardwired | 2,2,30s, 30s | Pointset
AHU Extract Fan VFD Frequency | AI | Number | R | AHUExtFanVFDFrq | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Panel Filter | AI | Number | R | AHUFrshAirPnlFltrDifPrSnsr | Hardwired | 2,2,30s, 30s | Pointset
AHU Supply Bag Filter | AI | Number | R | AHUFrshAirBagFltrDifPrSnsr | Hardwired | 2,2,30s, 30s | Pointset
AHU Intake Air Temperature | AI | Number | R | AHUintkAirTemp | Hardwired | 2,2,30s, 30s | Pointset
AHU Return Air Temperature | AI | Number | R | AHURTrnAirTemp | Hardwired | 2,2,30s, 30s | Pointset
AHU Return Bag Filter | AI | Number | R | AHURTrnAiBagFiltrDifPrSnsr | Hardwired | 2,2,30s, 30s | Pointset
AHU Return Panel Filter | AI | Number | R | AHURtrnAirPnlFltrDifPrSnsr | Hardwired | 2,2,30s, 30s | Pointset

## FCU
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
FCU Supply Air Temperature | AI | Num,0 | R | FCUSATemp | Hardwired | 2,2,30s, 30s | Pointset
FCU Hotwater Valve | AI | Num,0 | R | FCUHWV1v | Hardwired | 2,2,30s, 30s | Pointset
FCU Coldwater Valve | AI | Num,0 | R | FCUCWV1v | Hardwired | 2,2,30s, 30s | Pointset
Fan Command | AO/AI | Num,0 | R/W | FCUFanCmd | Hardwired | 2,2,30s, 30s | Pointset
Fan Temperature | AI | Num,0 | R | FCUFanTemp | Hardwired | 2,2,30s, 30s | Pointset
FCU Fan Power | AI | Num,0 | R | FCUFanPWR | Hardwired | 2,2,30s, 30s | Pointset
FCU Fan SpeedFdbk | AI | Num,0 | R | FCUFanSpdFDBK | Hardwired | 2,2,30s, 30s | Pointset
FCU Fan Status | AI | Num,0 | R | FCUFanStat | Hardwired | 2,2,30s, 30s | Pointset
FCU Return Air Temperature | AI | Num,0 | R | FCURATemp | Hardwired | 2,2,30s, 30s | Pointset
FCU Filter Differential Pressure Sensor | AI | Num,0 | R | FCUFltDifPrSnsr | Hardwired | 2,2,30s, 30s | Pointset
FCU zone temperature | AI | Num,0 | R | FCUZnTemp | Hardwired | 2,2,30s, 30s | Pointset
Temperature Setpoint | N/A | Num,0 | R/W | TempStPt | SoftPoint | 2,2,24hr, COV | State/Config
Cooling Setpoint | N/A | Num,0 | R/W | FCUOccCoolStPt | SoftPoint | 2,2,24hr, COV | State/Config
Unoccupied Cooling Setpoint | N/A | Num,0 | R | FCUUnoccCoolStPt | SoftPoint | 2,2,24hr, COV | State
Unoccupied Heating Setpoint | N/A | Num,0 | R | FCUUnoccHtgStPt | SoftPoint | 2,2,24hr, COV | State
Pressure Setpoint | N/A | Num,0 | R | PressStPt | SoftPoint | 2,2,24hr, COV | State
Flow Setpoint | N/A | Num,0 | R | FlowStPt | SoftPoint | 2,2,24hr, COV | State
Charge Level | AI | Num,0 | R | BatChrgLev | SoftPoint | 2,2,24hr, COV | State
Time to Discharge | AI | Num,0 | R | BatTmDschrg | SoftPoint | 2,2,24hr, COV | State
Time to Charge | AI | Num,0 | R | BatTmChrg | SoftPoint | 2,2,24hr, COV | State

## Cooling Towers
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Cooling Tower Fan Inverter Enable
Cooling Tower Fan Inverter Speed
Cooling Tower Fan Inverter Run Status
Cooling Tower Fan Inverter Fault status
Cooling Tower Condenser Water Primary Flow Temperature Sensor
Cooling Tower Condenser Water Primary Return Temperature Sensor
Cooling Tower Condenser Water Secondary Flow Temperature Sensor
Cooling Tower Condenser Water Secondary Return Temperature Sensor
Cooling Tower COND Isolation Valve Control
Cooling Tower COND Isolation Valve Status
Cooling Tower Spray Pump Start / Stop
Cooling Tower Blowdown Disable Override
Cooling Tower Sump Level
Emergency Knock Off (EKO) Button Status
Cooling Tower Basin Filter Pump Status
Cooling Tower Sump Level - Mechanical
Cooling Tower Non-Chemical
Cooling Tower Chemical Water Treatment Enable
Cooling Tower Chemical Water Treatment Status
Cooling Tower Chemical Water Treatment Alarm
Cooling Tower Chemical Water Conductivity
Cooling Tower Power Failure
Cooling Tower Enable Status
Cooling Tower VSD Alarm Status
Cooling Tower Trace Heating System Healthy
Cooling Tower Trace Heating System Tripped
Cooling Tower Common Fault

## Side Stream Filters
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Side Stream Filter Pump Enable
Side Stream Filter Invertor Enable
Side Stream Inverter Speed
Side Stream Filter Pressure Relief Bypass Valve Control
Side Stream Relief Bypass Valve Position

## Chillers
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Chiller Enable
Chiller Alarm
Chiller Status
Chiller CHW Primary Flow Temperature Sensor
Chiller CHW Primary Return Temperature Sensor
Chiller COND Primary Flow Temperature Sensor
Chiller COND Primary Return Temperature Sensor
Chiller Isolation Valve Control
Chiller Demand Limit (%)
Chiller Isolation Valve Feedback Status
CHW Differential Pressure Sensor
CHW Flow Rate Meter
Chiller CHW Supply Temp Set point
Fast Warm Up Bypass Valve Command
Chiller Head Pressure Control Signal (%) - From Chiller
Refrigerant Concentration
Refrigerant Monitor Alarm Level
Refrigerant Monitoring Alarm Fault
Refrigerant Pump Down
Power Failure
Common CHW Primary Flow Temperature Sensor
Common CHW Primary Return Temperature Sensor
Chiller Lock Out
Chiller % load
Differential Pressure Across Condenser
Differential Pressure Across Evaporator
Common CHW Primary Flow Temperature Sensor
Common CHW Primary Return Temperature Sensor

## Pressurisation Unit
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Pressurization Unit Common Fault
Pressurization Unit System High Pressure
Pressurization Unit System Low Pressure

## Vaccuum Degasser
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Vaccuum Degasser Common Fault
Side Stream Filter Invertor Enable
Side Stream Inverter Speed
Side Stream Filter Pressure Relief Bypass Valve Control
Side Stream Relief Bypass Valve Position

## Boilers
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State

## VT-Lift Cars
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Position | N/A | Number | R | LiftPos | SoftPoint | 2,2,24hr, COV | State
Load | N/A | Number | R | LiftLd | SoftPoint | 2,2,24hr, COV | State
Speed | N/A | Number | R | LiftSpd | SoftPoint | 2,2,24hr, COV | State
Door State | N/A | String (open, closed, opening, closing, waiting, blocked) | R | LiftDrState | SoftPoint | 2,2,24hr, COV | State
Travel to floor | N/A | Number | R/W | LiftTvlFlr | SoftPoint | 2,2,24hr, COV | State
Hold doors open | N/A | Boolean | R/W | LiftHldDrOp | SoftPoint | 2,2,24hr, COV | State
Lift sleep state | N/A | Boolean | R/W | LiftSlpState | SoftPoint | 2,2,24hr, COV | State
Display Interface | N/A | String | R/W | N/A | SoftPoint | 2,2,24hr, COV | State
% time availability | N/A | Number | R | LiftTmAvlblt | SoftPoint | 2,2,24hr, COV | State
% time planned maintenance | N/A | Number | R | LiftTmPlndMain | SoftPoint | 2,2,24hr, COV | State
% time out of service or under repair | N/A | Number | R | LiftTmOutSrv | SoftPoint | 2,2,24hr, COV | State
Total fault events per lift | N/A | Number | R | LiftTotFltEvntperLift | SoftPoint | 2,2,24hr, COV | State
Cumulative fault time per lift | N/A | Number | R | LiftCumFltTmperLift | SoftPoint | 2,2,24hr, COV | State
Log of call outs and service visits with date, time and duration | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Operation histories for each lift and lift group | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Journey, motor start and door operation counters for each lift | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Average response times for all landing calls (per lift group and per floor) | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Maximum response time for all landing calls (per lift group and per floor) | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Maximum response time for all landing calls (per lift group and per floor) | N/A | String | R

## Call Points
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Floors Selected | N/A | Number | R | LiftPos | SoftPoint | 2,2,24hr, COV | State
Display Interface | N/A | Number | R/W | LiftLd | SoftPoint | 2,2,24hr, COV | State

## Escalator
Property | Sensor Signal Type | Shadow Data Type | Read/Write | Point Abbreviation | Point Type | Healthwatch [Healthy Threshold, Unhealthy 'Threshold, Timeout, Interval] | MQTT Payload
ID -Credentials | N/A | String | R/W | InstGuid | SoftPoint | 2,2,24hr, COV | State/Config
local hostname | N/A | String | R/W | InstName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-type | N/A | String | R/W | TypeName | SoftPoint | 2,2,24hr, COV | State/Config
Instance-action ( IoTGW or IoTCtrl) | N/A | String | R | InstAct | SoftPoint | 2,2,24hr, COV | State
Local-ipv4 | N/A | String | R | IPAddr | SoftPoint | 2,2,24hr, COV | State
MacAddr | N/A | String | R | MACAddr | SoftPoint | 2,2,24hr, COV | State
Timestamp | N/A | String (RFC 3339) | R | Timestamp | SoftPoint | 2,2,24hr, COV | State
Fault Status | N/A | String | R | Flt | SoftPoint | 2,2,24hr, COV | State
Serial Number | N/A | String | R | SerNum | SoftPoint | 2,2,24hr, COV | State
Firmware Version | N/A | String | R | FirmVer | SoftPoint | 2,2,24hr, COV | State
Manufacturer | N/A | String | R | Man | SoftPoint | 2,2,24hr, COV | State
Running | N/A | Boolean | R/W | EsclRn | SoftPoint | 2,2,24hr, COV | State/Config
Direction | N/A | Boolean | R/W | EsclDir | SoftPoint | 2,2,24hr, COV | State/Config
Escalator low speed/energy save mode | N/A | Boolean | R/W | EsclLwSpd/EnrgySvMd | SoftPoint | 2,2,24hr, COV | State/Config
Escalator auto-walk mode | N/A | Boolean | R/W | EsclAutoWlkMd | SoftPoint | 2,2,24hr, COV | State/Config
% time availability | N/A | Number | R | EscTmAvlblt | SoftPoint | 2,2,24hr, COV | State
% time planned maintenance | N/A | Number | R | EscTmPlndMain | SoftPoint | 2,2,24hr, COV | State
% time out of service or under repair | N/A | Number | R | EscTmOutSrv | SoftPoint | 2,2,24hr, COV | State
Total fault events per escalator | N/A | Number | R | EscTotFltEvntperEsc | SoftPoint | 2,2,24hr, COV | State
Cumulative fault time per escalator | N/A | Number | R | EscCumFltTmperEsc | SoftPoint | 2,2,24hr, COV | State
Log of call outs and service visits with date, time and duration | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Operation histories for each lift and lift group | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State
Motor start and cumulative run-time counters for each escalator | N/A | String | R |  | SoftPoint | 2,2,24hr, COV | State